{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":31,"n_cols":13,"rows_kept":31,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","ARXM-R"]
[]
[]
[]
[]
["","","","","","ARXM25R5V1B","ARXM35R5V1B","ARXM50R2V1B","ARXM50R5V1B","ARXM60R5V1B","ARXM60R2V1B","ARXM71R5V1B","ARXM71R2V1B"]
["الأبعاد","الوحدة","","الارتفاع","mm","550","550","734","734","734","734","734","734"]
["","","","العرض","mm","765","765","954","954","954","954","954","954"]
["","","","العمق","mm","285","285","401","401","401","401","401","401"]
["الوزن","الوحدة","","","kg","32","32","49.0","49.0","49.0","49.0","49.0","49.0"]
["ضاغط","نوع","","","","ضاغط متأرجح محكم مانع للتسريب","ضاغط متأرجح محكم مانع للتسريب","ضاغط متأرجح محكم مانع للتسريب","ضاغط متأرجح محكم مانع للتسريب","ضاغط متأرجح محكم مانع للتسريب","ضاغط متأرجح محكم مانع للتسريب","ضاغط متأرجح محكم مانع للتسريب","ضاغط متأرجح محكم مانع للتسريب"]
["Operation range","Cooling","Ambient","Min.","درجة بمقياس الحوجلة الجافة","-10","-10","-10","-10 (4) (5), -10 (4) (5)","-10","-10","-10","-10"]
["","","","Max.","درجة بمقياس الحوجلة الجافة","50, 46","50, 46","50, 46","50 (4), 46 (5)","46","46","46","46"]
["","Heating","Ambient","Min.","°مئوية مقياس الحوجلة الرطبة","-15","-15","-15"]
["","","","Max.","°مئوية مقياس الحوجلة الرطبة","18","18","18"]
["Sound pressure level","Cooling","","Nom.","ديسيبل أمبير","46","49","48.0","48.0","48.0","48.0","52.0","52.0"]
["","Heating","","Nom.","ديسيبل أمبير","47","49","49.0","49.0","49.0","49.0","52.0","52.0"]
["سائل تبريد","السعة","","","kg","0.76","0.76","1.15","1.15","1.15","1.15","1.15","1.15"]
["","السعة","","","tCO2Eq","0.52","0.52","0.780","0.780","0.780","0.780","0.780","0.780"]
["","GWP","","","","675","675","675.0","675.0","675.0","675.0","675.0","675.0"]
["وصلات الأنابيب","طول الأنابيب","الحد الأعلى","الوحدة الخارجية - الوحدة الداخلية","م","20","20","30","30","30","30","30","30"]
["Piping connections","Additional refrigerant charge","","","kg/m","0.02 (for piping length exceeding 10m)","0.02 (for piping length exceeding 10m)","0.02 (for piping length exceeding 10m)","0.02 (for piping length exceeding 10m)","0.02 (for piping length exceeding 10m)","0.02 (for piping length exceeding 10m)","0.035 (لطول الأنابيب الذي يتجاوز 10م)","0.035 (لطول الأنابيب الذي يتجاوز 10م)"]
["","Level difference","IU - OU","Max.","م","15","15","20.0","20.0","20.0","20.0","20.0","20.0"]
["Standard Accessories","Installation manual","","","","1","1","1","1","1","1","1","1"]
["","Refrigerant charge label","","","","1","1","1","1","1","1","1","1"]
["","Multilingual fluorinated greenhouse gases labels","","","","1","1","1","1","1","1","1","1"]
["","Drain plug","","","","1","1","1","1","1","1","1","1"]
["Power supply","Frequency","","","Hz","50","50","50","50","50","50","50","50"]
["Standard Accessories","Drain cap","","","","","","3","3","3","3","3","3"]
["Notes","","","","","","","","(1) - ممكن فقط كتركيبة مع  CTXM*N2V1B، وATXM*N2V1B، وFTXM*N2V1B"]
["","","","","","","","","(2) - ممكن فقط كتركيبة مع CTXM*M2V1B، وATXM*M2V1B، وFTXM*M2V1B، وFVXM*FV1B، وFCAG*AVEB، وFFA*A2VEB9، وFBA*A2VEB9، وFHA*AVEB9، وFDXM*F3V1B9، وFNA*A2VEB9، وADEA*A2VEB·"]