{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":50,"n_cols":10,"rows_kept":50,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWFH-TZXSD"]
[]
[]
[]
[]
["","","","","","","EWFHH10TZXSD2","EWFHH11TZXSD2","EWFHH12TZXSD2","EWFHH13TZXSD2"]
["Cooling capacity","Nom.","","","","kW","1468.78","1564.68","1682.27","1812.01"]
["Capacity control","طريقة","","","","","بدون تدرج","بدون تدرج","بدون تدرج","بدون تدرج"]
["","Minimum capacity","","","","%","10","13.5","12.5","11.5"]
["Power input","Cooling","","","Nom.","kW","416.08","422.09","463.18","521.59"]
["EER","","","","","","3.53","3.71","3.63","3.47"]
["قيمة حمل الجزء المتكامل","","","","","","6.436","6.376","6.481","6.426"]
["SEER","","","","","","5.997","5.645","5.693","5.758"]
["الأبعاد","الوحدة","","","العمق","mm","11200","11200","12280","13360"]
["","","","","الارتفاع","mm","2553","2553","2553","2553"]
["","","","","العرض","mm","2238","2238","2238","2238"]
["الوزن","Operation weight","","","","kg","11223","11906","12491","13081"]
["","الوحدة","","","","kg","8383","9051","9561","10070"]
["الغلاف","اللون","","","","","Ivory white","Ivory white","Ivory white","Ivory white"]
["الغلاف","المادة","","","","","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet"]
["Water heat exchanger - evaporator","Type","","","","","Shell and tube","Shell and tube","Shell and tube","Shell and tube"]
["","Water volume","","","","l","1011","1011","1011","1011"]
["مبادل حراري مائي - مبخر","انخفاض ضغط الماء","","التبريد","الإسمي","كيلو باسكال","30.4","48.85","54.18","41.49"]
["Air heat exchanger","Type","","","","","قناة ميكرووية","قناة ميكرووية","قناة ميكرووية","قناة ميكرووية"]
["Fan","الكمية","","","","","20","20","22","24"]
["مروحة","النوع","","","","","مروحة توجيه","مروحة توجيه","مروحة توجيه","مروحة توجيه"]
["المروحة","معدل تدفق الهواء","","التبريد","الإسمي","ل/ثا","112550","112550","123805","135060"]
["محرك المروحة","محرك","","","","","بدون مسفرات","بدون مسفرات","بدون مسفرات","بدون مسفرات"]
["Compressor","Quantity","","","","","2","2","2","2"]
["","Type","","","","","Screw compressor","Screw compressor","Screw compressor","Screw compressor"]
["Operation range","Air side","","Cooling","Min.","درجة بمقياس الحوجلة الجافة","-20","-20","-20","-20"]
["","","","","Max.","درجة بمقياس الحوجلة الجافة","46","46","46","46"]
["","Water side","","Cooling","Min.","درجة بمقياس الحوجلة الجافة","4","4","4","4"]
["","","","المبخر","القصوى","درجة بمقياس الحوجلة الجافة","18","18","18","18"]
["Sound power level","Cooling","","","Nom.","dBA","104.7","102.7","103.6","104.5"]
["Sound pressure level","Cooling","","","Nom.","dBA","82.2","80.1","80.8","81.4"]
["سائل تبريد","النوع","","","","","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)"]
["Refrigerant","GWP","","","","","7","7","7","7"]
["","Charge","","","","kg","150","165","175","190"]
["","Circuits","","","Quantity","","2","2","2","2"]
["Piping connections","مدخل/مخرج الماء للمبخر (القطر الخارجي)","","","","","273","273","273","273"]
["وحدة التزويد بالطاقة","الطور","","","","","3","3","3","3"]
["Power supply","Power supply-=-Frequency","","","Frequency","","50","50","50","50"]
["","Power supply-=-Voltage","","","Voltage","","400","400","400","400"]
["","Voltage range","","الحد الأدنى","Min.","","-10","-10","-10","-10"]
["","","","الحد الأقصى","Max.","","10","10","10","10"]
["الوحدة","تيار بدء التشغيل","","الوحدة-=-تيار بدء التشغيل-=-حد أقصى","حد أقصى","","0","0","0","0"]
["","تيار العمل","التبريد","الوحدة-=-تيار العمل-=-التبريد-=-الاسمي","الاسمي","","661","678","739","826"]
["","","","الوحدة-=-تيار العمل-=-حد أقصى","حد أقصى","","787","902","992","1090"]
["Unit","Unit-=-Max unit current for wires sizing","","","Max unit current for wires sizing","","866","992","1091","1198"]