{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":58,"n_cols":14,"rows_kept":58,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWAD-C-PR"]
[]
[]
[]
[]
["","","","","","EWAD810C-PR","EWAD880C-PR","EWAD960C-PR","EWADC10C-PR","EWADC11C-PR","EWADC13C-PR","EWADC14C-PR","EWADC15C-PR","EWADC16C-PR"]
["Cooling capacity","Nom.","","","kW","805.8","871.1","953.8","1,048","1,126","1,246","1,353","1,436","1,515"]
["Capacity control","Method","","","","Fixed","Fixed","Fixed","Fixed","Fixed","Fixed","Fixed","Fixed","Fixed"]
["","Minimum capacity","","","%","12.5","12.5","12.5","12.5","12.5","12.5","12.5","12.5","12.5"]
["Power input","Cooling","","Nom.","kW","221.9","248.3","274.5","303.4","335.1","368.5","402.2","433.9","467.1"]
["EER","","","","","3.631","3.508","3.474","3.457","3.363","3.381","3.364","3.311","3.245"]
["IPLV","","","","","5.07","4.89","4.89","4.92","4.82","4.81","4.85","4.85","4.79"]
["SEER","","","","","4.5","4.5","5.0","4.5","4.4","4.4","4.4","4.5","4.5"]
["Dimensions","Unit","","Depth","mm","8,985","8,985","8,985","9,885","9,885","11,185","12,085","12,085","12,085"]
["","","","Height","mm","2,540","2,540","2,540","2,540","2,540","2,540","2,540","2,540","2,540"]
["","","","Width","mm","2,285","2,285","2,285","2,285","2,285","2,285","2,285","2,285","2,285"]
["Weight","Operation weight","","","kg","8,420","8,420","8,990","9,620","9,880","10,670","11,010","11,010","11,010"]
["","Unit","","","kg","7,820","7,820","7,950","8,580","8,840","10,380","10,720","10,720","10,720"]
["Casing","Colour","","","","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white"]
["","Material","","","","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet"]
["Air heat exchanger","Type","","","","High efficiency fin and tube type – Copper Aluminum","High efficiency fin and tube type – Copper Aluminum","High efficiency fin and tube type – Copper Aluminum","High efficiency fin and tube type – Copper Aluminum","High efficiency fin and tube type – Copper Aluminum","High efficiency fin and tube type – Copper Aluminum","High efficiency fin and tube type – Copper Aluminum","High efficiency fin and tube type – Copper Aluminum","High efficiency fin and tube type – Copper Aluminum"]
["Fan","Quantity","","","","18","18","18","20","20","22","24","24","24"]
["","Type","","","","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller"]
["Fan motor","Drive","","","","DOL","DOL","DOL","DOL","DOL","DOL","DOL","DOL","DOL"]
["Compressor","Quantity","","","","2","2","2","2","2","2","2","2","2"]
["","Type","","","","Asymmetric single screw compressor","Asymmetric single screw compressor","Asymmetric single screw compressor","Asymmetric single screw compressor","Asymmetric single screw compressor","Asymmetric single screw compressor","Asymmetric single screw compressor","Asymmetric single screw compressor","Asymmetric single screw compressor"]
["","Starting method","","","","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta"]
["Operation range","Air side","Cooling","Min.","°CDB","-18","-18","-18","-18","-18","-18","-18","-18","-18"]
["","","","Max.","°CDB","52","52","52","52","52","52","52","52","52"]
["","Water side","Evaporator","Min.","°CDB","-8","-8","-8","-8","-8","-8","-8","-8","-8"]
["","","","Max.","°CDB","15","15","15","15","15","15","15","15","15"]
["Sound power level","Cooling","","Nom.","dBA","93","93","93","93","94","94","94","95","95"]
["Sound pressure level","Cooling","","Nom.","dBA","71","71","71","72","72","72","72","72","73"]
["Refrigerant","Type","","","","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a"]
["","GWP","","","","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430"]
["","Charge","","","kg","204","204","204","230","240","275","280","280","280"]
["","Circuits","","Quantity","","2","2","2","2","2","2","2","2","2"]
["Piping connections","Evaporator water inlet/outlet (OD)","","","","219.1mm","219.1mm","273mm","273mm","273mm","273mm","273mm","273mm","273mm"]
["Power supply","Phase","","","","3~","3~","3~","3~","3~","3~","3~","3~","3~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","400","400","400","400","400","400","400","400","400"]
["","Voltage range","","Min.","%","-10","-10","-10","-10","-10","-10","-10","-10","-10"]
["","","","Max.","%","10","10","10","10","10","10","10","10","10"]
["Unit","Starting current","","Max","A","618","653","653","917","964","1,020","1,020","1,063","1,076"]
["","Running current","Cooling","Nom.","A","375","416","461","506","555","614","671","717","764"]
["","","","Max","A","509","552","596","660","719","788","858","911","964"]
["","Max unit current for wires sizing","","","A","555","603","651","721","785","861","937","996","1,054"]
["Notes","","","","","(1) - Performance calculations according to EN 14511","(1) - Performance calculations according to EN 14511","(1) - Performance calculations according to EN 14511","(1) - Performance calculations according to EN 14511","(1) - Performance calculations according to EN 14511","(1) - Performance calculations according to EN 14511","(1) - Performance calculations according to EN 14511","(1) - Performance calculations according to EN 14511","(1) - Performance calculations according to EN 14511"]
["","","","","","(2) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units","(2) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units","(2) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units","(2) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units","(2) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units","(2) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units","(2) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units","(2) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units","(2) - Sound power level (at standard conditions) is measured in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units"]
["","","","","","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%."]
["","","","","","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %"]
["","","","","","(5) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(5) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(5) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(5) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(5) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(5) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(5) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(5) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(5) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current."]
["","","","","","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current"]
["","","","","","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage."]
["","","","","","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1"]
["","","","","","(9) - Fluid: Water","(9) - Fluid: Water","(9) - Fluid: Water","(9) - Fluid: Water","(9) - Fluid: Water","(9) - Fluid: Water","(9) - Fluid: Water","(9) - Fluid: Water","(9) - Fluid: Water"]
["","","","","","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS)."]
["","","","","","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels."]