{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":43,"n_cols":12,"rows_kept":43,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWAD-TZXSC2"]
[]
[]
[]
[]
["","","","","","EWADC12TZXSC2","EWADC14TZXSC2","EWADC15TZXSC2","EWADH16TZXSC2","EWADC11TZXSC2","EWADH17TZXSC2","EWADH12TZXSC2"]
["Cooling capacity","Nom.","","","kW","1,206","1,399","1,539","1,667","1,124","1,780","1,280"]
["Capacity control","Method","","","","Variable","Variable","Variable","Variable","Variable","Variable","Variable"]
["","Minimum capacity","","","%","12.5","12.5","12.5","12.5","12.5","12.5","12.5"]
["Power input","Cooling","","Nom.","kW","375.9","431.7","478.8","524.7","354","575.4","401.6"]
["EER","","","","","3.21","3.24","3.22","3.18","3.17","3.09","3.19"]
["IPLV","","","","","5.58","5.79","5.7","5.66","5.54","5.65","5.54"]
["SEER","","","","","5.35","5.37","5.39","5.43","5.36","5.39","5.35"]
["Dimensions","Unit","","Depth","mm","11,402","11,402","12,302","13,202","10,510","14,104","12,302"]
["","","","Height","mm","2,540","2,540","2,540","2,540","2,540","2,540","2,540"]
["","","","Width","mm","2,282","2,282","2,282","2,282","2,282","2,282","2,282"]
["Weight","Operation weight","","","kg","11,123","11,727","12,145","12,575","9,879","13,048","11,526"]
["","Unit","","","kg","10,112","10,716","11,134","11,564","9,322","12,037","10,515"]
["Casing","Colour","","","","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white"]
["","Material","","","","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet"]
["Air heat exchanger","Type","","","","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel"]
["Fan","Quantity","","","","24","24","26","28","22","30","26"]
["","Type","","","","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller"]
["Fan motor","Drive","","","","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven"]
["Compressor","Quantity","","","","2","2","2","2","2","2","2"]
["","Type","","","","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor"]
["","Starting method","","","","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven"]
["Sound power level","Cooling","","Nom.","dBA","96","101","101","102","95","102","97"]
["Sound pressure level","Cooling","","Nom.","dBA","73","78","78","79","73","79","74"]
["Refrigerant","Type","","","","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a"]
["","GWP","","","","1,430","1,430","1,430","1,430","1,430","1,430","1,430"]
["","Charge","","","kg","200","200","220","250","175","270","220"]
["","Circuits","","Quantity","","2","2","2","2","2","2","2"]
["Piping connections","Evaporator water inlet/outlet (OD)","","","","273mm","273mm","273mm","273mm","219.1mm","273mm","219.1mm"]
["Power supply","Phase","","","","3~","3~","3~","3~","3~","3~","3~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50"]
["","Voltage","","","V","400","400","400","400","400","400","400"]
["","Voltage range","","Min.","%","-1","-1","-1","-1","-1","-1","-1"]
["","","","Max.","%","-1","-1","-1","-1","-1","-1","-1"]
["Unit","Starting current","","Max","A","0.0","0.0","0.0","0.0","0.0","0.0","0.0"]
["","Running current","Cooling","Nom.","A","647.1","735.8","806.6","874.7","608.8","957.5","686.1"]
["","","","Max","A","939","1,085","1,124","1,218","918","1,313","994"]
["","Max unit current for wires sizing","","","A","1,033","1,194","1,236","1,340","1,010","1,444","1,093"]