{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":45,"n_cols":6,"rows_kept":45,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FDQ-C"]
[]
[]
[]
[]
["","","","","FDQ125C5VEB","FDQ125C7VEB"]
["Sound pressure level","Heating","High","dBA","40","40"]
["","","Low","dBA","33","33"]
["","Cooling","Low","dBA","33","33"]
["","","High","dBA","40","40"]
["Control systems","Wired remote control","","","BRC1D52, BRC1E53A, BRC1E53B, BRC1E53C","BRC1D52, BRC1E53A, BRC1E53B, BRC1E53C, BRC1D528"]
["","Infrared remote control","","","BRC4C65","BRC4C65"]
["Cooling capacity","Total capacity","Nom.","kW","12.5 (1)","12.5"]
["Piping connections","Liquid","OD","mm","9.52","9.52"]
["","Gas","OD","mm","15.9","15.9"]
["","Drain","","","VP25 (I.D. 25/O.D. 32)","VP25 (I.D. 25/O.D. 32)"]
["Required ceiling void >","mm","","","350","350"]
["Power input","Cooling","Nom.","kW","0.35"]
["","Heating","Nom.","kW","0.35"]
["Sound power level","Cooling","","dBA","66","66"]
["Dimensions","Unit","Width","mm","1,400","1,400"]
["","","Depth","mm","700","700"]
["","","Height","mm","300","300"]
["Casing","Material","","","","Galvanised steel"]
["","Colour","","","Not painted (galvanised)","Not painted"]
["Weight","Unit","","kg","45","45"]
["Fan","External static pressure","High","Pa","200","200"]
["","","Nom.","Pa","50","50"]
["Drain-up height","mm","","","625","625"]
["Decoration panel","Weight","","kg","6.5","6.5"]
["","Model","","","BYBS125DJW1","BYBS125DJW1"]
["","Dimensions","Height","mm","55","55"]
["","","Depth","mm","500","500"]
["","","Width","mm","1,500","1,500"]
["","Colour","","","White (10Y9/0.5)","White (10Y9/0.5)"]
["Heating capacity","Total capacity","Nom.","kW","14.0 (2)","14.0"]
["Power supply","Phase","","","1~","1~"]
["","Name","","","VE","VE"]
["","Frequency","","Hz","50/60","50/60"]
["","Voltage","","V","220-240/220","220-240/220"]
["Notes","","","","(1) - Cooling: indoor temp. 27°CDB, 19.0°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m"]
["","","","","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat."]
["","","","","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - The sound pressure values are mentioned for a unit installed with rear suction."]
["","","","","(4) - The sound pressure values are mentioned for a unit installed with rear suction.","(4) - PED unit category: excluded from scope of PED due to article 1, item 3.6 of 97/23/EC"]
["","","","","(5) - PED unit category: excluded from scope of PED due to article 1, item 3.6 of 97/23/EC","(5) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal); level difference: 0m"]