{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":63,"n_cols":19,"rows_kept":63,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWD-AF"]
[]
[]
[]
[]
["","","","","","FWD04AAFN6V3","FWD04ACFN6V3","FWD06AAFN6V3","FWD06ACFN6V3","FWD08AAFN6V3","FWD08ACFN6V3","FWD10AAFN6V3","FWD10ACFN6V3","FWD12AAFN6V3","FWD12ACFN6V3","FWD16AAFN6V3","FWD16ACFN6V3","FWD18AAFN6V3","FWD18ACFN6V3"]
["Control systems","Wired remote control","","","","FWEC1A, FWEC2A, FWEC3A","","FWEC1A, FWEC2A, FWEC3A","","FWEC1A, FWEC2A, FWEC3A","","FWEC1A, FWEC2A, FWEC3A","","FWEC1A, FWEC2A, FWEC3A","","FWEC1A, FWEC2A, FWEC3A","","FWEC1A, FWEC2A, FWEC3A"]
["Piping connections","Drain","","OD","mm","16","","16","","16","","16","","16","","16","","16"]
["Dimensions","Unit","","Width","mm","754","","964","","1,174","","1,174","","1,174","","1,384","","1,384"]
["","","","Depth","mm","559","","559","","559","","559","","718","","718","","718"]
["","","","Height","mm","280","","280","","280","","280","","352","","352","","352"]
["Casing","Colour","","","","Not painted (galvanised)","","Not painted (galvanised)","","Not painted (galvanised)","","Not painted (galvanised)","","Not painted (galvanised)","","Not painted (galvanised)","","Not painted (galvanised)"]
["Weight","Unit","","","kg","35","","43","","50","","52","","71","","83","","86"]
["Fan","Air flow rate","","High","m³/h","800","","1,250","","1,600","","1,600","","2,200","","3,000","","3,000"]
["Current input","High","","","A","0.95","","1.58","","1.97","","1.97","","3.21","","5.37","","5.37"]
["","Low","","","A","0.57","","1.18","","1.20","","1.20","","1.50","","3.26","","3.26"]
["Power supply","Phase","","","","1~","","1~","","1~","","1~","","1~","","1~","","1~"]
["","Frequency","","","Hz","50","","50","","50","","50","","50","","50","","50"]
["","Voltage","","","V","230","","230","","230","","230","","230","","230","","230"]
["Notes","","","","","(1) - Rating conditions 4-pipe: air 27°CDB - 19°CWB - entering water 7°C - leaving water 12°C at nominal air flow and ESP","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Rating conditions 4-pipe: air 27°CDB - 19°CWB - entering water 7°C - leaving water 12°C at nominal air flow and ESP","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Rating conditions 4-pipe: air 27°CDB - 19°CWB - entering water 7°C - leaving water 12°C at nominal air flow and ESP","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Rating conditions 4-pipe: air 27°CDB - 19°CWB - entering water 7°C - leaving water 12°C at nominal air flow and ESP","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Rating conditions 4-pipe: air 27°CDB - 19°CWB - entering water 7°C - leaving water 12°C at nominal air flow and ESP","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Rating conditions 4-pipe: air 27°CDB - 19°CWB - entering water 7°C - leaving water 12°C at nominal air flow and ESP","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Rating conditions 4-pipe: air 27°CDB - 19°CWB - entering water 7°C - leaving water 12°C at nominal air flow and ESP","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K."]
["","","","","","(2) - Rating conditions 4-pipe: air 20°CDB - entering water 70°C - leaving water 60°C at nominal air flow and ESP","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(2) - Rating conditions 4-pipe: air 20°CDB - entering water 70°C - leaving water 60°C at nominal air flow and ESP","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(2) - Rating conditions 4-pipe: air 20°CDB - entering water 70°C - leaving water 60°C at nominal air flow and ESP","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(2) - Rating conditions 4-pipe: air 20°CDB - entering water 70°C - leaving water 60°C at nominal air flow and ESP","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(2) - Rating conditions 4-pipe: air 20°CDB - entering water 70°C - leaving water 60°C at nominal air flow and ESP","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(2) - Rating conditions 4-pipe: air 20°CDB - entering water 70°C - leaving water 60°C at nominal air flow and ESP","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(2) - Rating conditions 4-pipe: air 20°CDB - entering water 70°C - leaving water 60°C at nominal air flow and ESP","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K."]
["","","","","","(3) - Maximum Power input at 0Pa ESP","(3) - Sound power level according to ISO3741","(3) - Maximum Power input at 0Pa ESP","(3) - Sound power level according to ISO3741","(3) - Maximum Power input at 0Pa ESP","(3) - Sound power level according to ISO3741","(3) - Maximum Power input at 0Pa ESP","(3) - Sound power level according to ISO3741","(3) - Maximum Power input at 0Pa ESP","(3) - Sound power level according to ISO3741","(3) - Maximum Power input at 0Pa ESP","(3) - Sound power level according to ISO3741","(3) - Maximum Power input at 0Pa ESP","(3) - Sound power level according to ISO3741"]
["","","","","","(4) - Sound level at 0Pa ESP","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - Sound level at 0Pa ESP","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - Sound level at 0Pa ESP","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - Sound level at 0Pa ESP","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - Sound level at 0Pa ESP","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - Sound level at 0Pa ESP","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - Sound level at 0Pa ESP","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit."]
["","","","","","(5) - Current input at 0Pa ESP","","(5) - Current input at 0Pa ESP","","(5) - Current input at 0Pa ESP","","(5) - Current input at 0Pa ESP","","(5) - Current input at 0Pa ESP","","(5) - Current input at 0Pa ESP","","(5) - Current input at 0Pa ESP"]
["Cooling capacity (standard conditions)","Sensible capacity 4-pipe","","Low","kW","","2.09 (1)","","3.60 (1)","","4.79 (1)","","5.17 (1)","","6.29 (1)","","8.58 (1)","","9.34 (1)"]
["","","","High","kW","","2.80 (1)","","4.08 (1)","","5.94 (1)","","6.46 (1)","","9.06 (1)","","12.14 (1)","","13.41 (1)"]
["","Total capacity 4-pipe","","Low","kW","","2.73 (1)","","4.92 (1)","","5.97 (1)","","6.61 (1)","","8.33 (1)","","11.59 (1)","","12.87 (1)"]
["","","","High","kW","","3.62 (1)","","5.60 (1)","","7.20 (1)","","8.10 (1)","","11.66 (1)","","15.84 (1)","","17.66 (1)"]
["Heating capacity (standard conditions)","Capacity 4-pipe","","Low","kW","","3.23 (3)","","5.25 (3)","","7.02 (3)","","6.99 (3)","","10.86 (3)","","14.88 (3)","","14.79 (3)"]
["","","","High","kW","","3.91 (3)","","5.72 (3)","","7.99 (3)","","7.94 (3)","","14.43 (3)","","19.30 (3)","","19.20 (3)"]
["Power input","Low","","","kW","","0.14","","0.35","","0.29","","0.29","","0.37","","0.87","","0.87"]
["","High","","","kW","","0.265","","0.460","","0.505","","0.505","","0.750","","1.300","","1.300"]
["Dimensions","Unit","","Height","mm","","559","","559","","559","","559","","718","","718","","718"]
["","","","Width","mm","","754","","964","","1170","","1170","","1170","","1380","","1380"]
["","","","Depth","mm","","280","","280","","280","","280","","353","","353","","353"]
["Weight","Unit","","","kg","","34.7","","43.2","","50.3","","51.7","","70.9","","83.4","","85.9"]
["Fan","Air flow rate","","Low","m³/h","","532","","1004","","1194","","1186","","1466","","2084","","2065"]
["","","","High","m³/h","","794","","1212","","1573","","1550","","2328","","3186","","3155"]
["","Available static pressure","","Low","Pa","","38","","41","","38","","38","","30","","31","","32"]
["","","","High","Pa","","67","","59","","67","","66","","78","","76","","74"]
["Total sound power level","Low","","","dBA","","54 (4)","","61 (4)","","62 (4)","","62 (4)","","60 (4)","","69 (4)","","69 (4)"]
["","High","","","dBA","","66 (4)","","69 (4)","","72 (4)","","72 (4)","","74 (4)","","78 (4)","","78 (4)"]
["Sound pressure level","Low","","","dBA","","49 (5)","","56 (5)","","57 (5)","","57 (5)","","55 (5)","","64 (5)","","64 (5)"]
["","High","","","dBA","","61 (5)","","64 (5)","","67 (5)","","67 (5)","","69 (5)","","73 (5)","","73 (5)"]
["Water flow","Cooling","","Low","l/h","","491 (1)","","904 (1)","","1075 (1)","","1185 (1)","","1493 (1)","","2138 (1)","","2358 (1)"]
["","","","High","l/h","","666 (1)","","1040 (1)","","1322 (1)","","1476 (1)","","2130 (1)","","2940 (1)","","3254 (1)"]
["","Heating","","Low","l/h","","283 (3)","","460 (3)","","614 (3)","","612 (3)","","950 (3)","","1302 (3)","","1295 (3)"]
["","","","High","l/h","","342 (3)","","501 (3)","","700 (3)","","695 (3)","","1264 (3)","","1690 (3)","","1680 (3)"]
["","Water pressure drop","Cooling","Low","kPa","","10 (1)","","18 (1)","","16 (1)","","10 (1)","","15 (1)","","21 (1)","","27 (1)"]
["","","","High","kPa","","17 (1)","","23 (1)","","23 (1)","","15 (1)","","28 (1)","","36 (1)","","48 (1)"]
["","","Heating","Low","kPa","","5 (3)","","12 (3)","","8 (3)","","20 (3)","","6 (3)","","12 (3)","","13 (3)"]
["","","","High","kPa","","7 (3)","","14 (3)","","10 (3)","","25 (3)","","10 (3)","","21 (3)","","20 (3)"]
["Allowed water temperature","Cooling","","Min.","°C","","5","","5","","5","","5","","5","","5","","5"]
["","","","Max.","°C","","95.0","","95.0","","95.0","","95.0","","95.0","","95.0","","95.0"]
["","Heating","","Min.","°C","","5.00","","5.00","","5.00","","5.00","","5.00","","5.00","","5.00"]
["","","","Max.","°C","","95.000","","95.000","","95.000","","95.000","","95.000","","95.000","","95.000"]
["Piping connections","Drain","","OD","mm","","17","","17","","17","","17","","17","","17","","17"]
["Water connections","Primary coil","","","in","","3/4\"","","3/4\"","","3/4\"","","3/4\"","","1/2\"","","1/2\"","","1/2\""]
["","Additional coil","","","in","","3/4\"","","3/4\"","","3/4\"","","3/4\"","","1/2\"","","1/2\"","","1/2\""]
["Power supply","Type","","","","","230 / 1 / 50","","230 / 1 / 50","","230 / 1 / 50","","230 / 1 / 50","","230 / 1 / 50","","230 / 1 / 50","","230 / 1 / 50"]
["","Phase","","","","","1~","","1~","","1~","","1~","","1~","","1~","","1~"]
["","Frequency","","","Hz","","50","","50","","50","","50","","50","","50","","50"]
["","Voltage","","","V","","230","","230","","230","","230","","230","","230","","230"]