{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":48,"n_cols":17,"rows_kept":48,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FXLQ-P"]
[]
[]
[]
[]
["","","","","","FXLQ20P5VEB","FXLQ25P5VEB","FXLQ32P5VEB","FXLQ40P5VEB","FXLQ40P2VEB","FXLQ50P5VEB","FXLQ63P5VEB","FXLQ20P2VEB (Archived)","FXLQ25P2VEB (Archived)","FXLQ32P2VEB (Archived)","FXLQ50P2VEB (Archived)","FXLQ63P2VEB (Archived)"]
["Sound pressure level","Heating","","At high fan speed","dBA","35","35","35","38","38","39","40","35","35","35","39","40"]
["","","","At low fan speed","dBA","32","32","32","33","33","34","35","32","32","32","34","35"]
["","Cooling","","At low fan speed","dBA","32","32","32","33","33","34","35","32","32","32","34","35"]
["","","","At high fan speed","dBA","35","35","35","38","38","39","40","35","35","35","39","40"]
["Refrigerant","GWP","","","","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5"]
["","Type","","","","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A"]
["Power input - 50Hz","Cooling","","At high fan speed","kW","0.05 (1)","0.05 (1)","0.09 (1)","0.09 (1)","0.090 (1)","0.11 (1)","0.11 (1)","0.05 (1)","0.05 (1)","0.09 (1)","0.11 (1)","0.11 (1)"]
["","Heating","","At high fan speed","kW","0.05 (2)","0.05 (2)","0.09 (2)","0.09 (2)","0.090 (2)","0.11 (2)","0.11 (2)","0.05 (2)","0.05 (2)","0.09 (2)","0.11 (2)","0.11 (2)"]
["Cooling capacity","Total capacity","","At high fan speed","kW","2.2 (1)","2.8 (1)","3.6 (1)","4.5 (1)","4.5 (1)","5.6 (1)","7.1 (1)","2.2 (1)","2.8 (1)","3.6 (1)","5.6 (1)","7.1 (1)"]
["Piping connections","Liquid","","OD","mm","6.35","6.35","6.35","6.35","6.35","6.35","6.35","6.35","6.35","6.35","6.35","9.52"]
["","","","Type","","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection"]
["","Gas","","OD","mm","12.7","12.7","12.7","12.7","12.7","12.7","15.9","12.7","12.7","12.7","12.7","15.9"]
["","","","Type","","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection"]
["","Drain","","","","O.D. 21 (Vinyl chloride)","O.D. 21 (Vinyl chloride)","O.D. 21 (Vinyl chloride)","O.D. 21 (Vinyl chloride)","O.D. 21 (Vinyl chloride)","O.D. 21 (Vinyl chloride)","O.D. 21 (Vinyl chloride)","O.D. 21 (Vinyl chloride)","O.D. 21 (Vinyl chloride)","O.D. 21 (Vinyl chloride)","O.D. 21 (Vinyl chloride)","O.D. 21 (Vinyl chloride)"]
["Sound power level","Cooling","","At high fan speed","dBA","54","54","54","57","","58","59","54","54","54","58","59"]
["Air filter","Type","","","","Resin net","Resin net","Resin net","Resin net","Resin net","Resin net","Resin net","Resin net","Resin net","Resin net","Resin net","Resin net"]
["Dimensions","Unit","","Width","mm","1,000","1,000","1,140","1,140","1,140","1,420","1,420","1,000","1,000","1,140","1,420","1,420"]
["","","","Depth","mm","232","232","232","232","232","232","232","232","232","232","232","232"]
["","","","Height","mm","600","600","600","600","600","600","600","600","600","600","600","600"]
["Casing","Colour","","","","Fresh white (RAL9010) / Dark grey (RAL7012)","Fresh white (RAL9010) / Dark grey (RAL7012)","Fresh white (RAL9010) / Dark grey (RAL7012)","Fresh white (RAL9010) / Dark grey (RAL7012)","Fresh white (RAL9010) / Dark grey (RAL7011)","Fresh white (RAL9010) / Dark grey (RAL7012)","Fresh white (RAL9010) / Dark grey (RAL7012)","Fresh white (RAL9010) / Dark grey (RAL7011)","Fresh white (RAL9010) / Dark grey (RAL7011)","Fresh white (RAL9010) / Dark grey (RAL7011)","Fresh white (RAL9010) / Dark grey (RAL7011)","Fresh white (RAL9010) / Dark grey (RAL7011)"]
["Weight","Unit","","","kg","27","27","32","32","32","38","38","27","27","32","38","38"]
["Fan","Air flow rate - 50Hz","Cooling","At high fan speed","m³/min","7","7","8","11","11","14","16","7","7","8","14","16"]
["","","","At low fan speed","m³/min","6.0","6.0","6.0","8.5","8.5","11.0","12.0","6.0","6.0","6.0","11.0","12.0"]
["","Air flow rate - 60Hz","Cooling","High","m³/min","","","","","11"]
["","","","Low","m³/min","","","","","8.5"]
["Heating capacity","Total capacity","","At high fan speed","kW","2.5 (2)","3.2 (2)","4.0 (2)","5.0 (2)","5.0 (2)","6.3 (2)","8.0 (2)","2.5 (2)","3.2 (2)","4.0 (2)","6.3 (2)","8.0 (2)"]
["Current - 50Hz","Maximum fuse amps (MFA)","","","A","15","15","15","15","15","15","15","15","15","15","15","15"]
["Power supply","Phase","","","","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~"]
["","Name","","","","VE","VE","VE","VE","VE","VE","VE","VE","VE","VE","VE","VE"]
["","Frequency","","","Hz","50/60","50/60","50/60","50/60","50/60","50/60","50/60","50/60","50/60","50/60","50/60","50/60"]
["","Voltage","","","V","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)"]
["","","","","","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)"]
["","","","","","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat."]
["","","","","","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA"]
["","","","","","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA"]
["","","","","","(8) - Next lower standard fuse rating minimum 15A","(8) - Next lower standard fuse rating minimum 15A","(8) - Next lower standard fuse rating minimum 15A","(8) - Next lower standard fuse rating minimum 15A","(8) - Next lower standard fuse rating minimum 15A","(8) - Next lower standard fuse rating minimum 15A","(8) - Next lower standard fuse rating minimum 15A","(8) - Next lower standard fuse rating minimum 15A","(8) - Next lower standard fuse rating minimum 15A","(8) - Next lower standard fuse rating minimum 15A","(8) - Next lower standard fuse rating minimum 15A","(8) - Next lower standard fuse rating minimum 15A"]
["","","","","","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA"]
["","","","","","(10) - Contains fluorinated greenhouse gases","(10) - Contains fluorinated greenhouse gases","(10) - Contains fluorinated greenhouse gases","(10) - Contains fluorinated greenhouse gases","(10) - Instead of a fuse, use a circuit breaker","(10) - Contains fluorinated greenhouse gases","(10) - Contains fluorinated greenhouse gases","(10) - Instead of a fuse, use a circuit breaker","(10) - Instead of a fuse, use a circuit breaker","(10) - Instead of a fuse, use a circuit breaker","(10) - Instead of a fuse, use a circuit breaker","(10) - Instead of a fuse, use a circuit breaker"]
["","","","","","(11) - Instead of a fuse, use a circuit breaker","(11) - Instead of a fuse, use a circuit breaker","(11) - Instead of a fuse, use a circuit breaker","(11) - Instead of a fuse, use a circuit breaker","(11) - Contains fluorinated greenhouse gases","(11) - Instead of a fuse, use a circuit breaker","(11) - Instead of a fuse, use a circuit breaker","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases"]