{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":58,"n_cols":13,"rows_kept":58,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FXSQ-MVE"]
[]
[]
[]
[]
["","","","","FXSQ20MVE9","FXSQ25MVE9","FXSQ32MVE9","FXSQ40MVE9","FXSQ50MVE9","FXSQ63MVE9","FXSQ80MVE9","FXSQ100MVE9","FXSQ125MVE9"]
["Standard Accessories","Operation manual","","","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual"]
["","Installation manual","","","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual"]
["","Paper pattern for installation","","","Paper pattern for installation","Paper pattern for installation","Paper pattern for installation","Paper pattern for installation","Paper pattern for installation","Paper pattern for installation","Paper pattern for installation","Paper pattern for installation","Paper pattern for installation"]
["","Drain hose","","","Drain hose","Drain hose","Drain hose","Drain hose","Drain hose","Drain hose","Drain hose","Drain hose","Drain hose"]
["","Clamp metal","","","Clamp metal","Clamp metal","Clamp metal","Clamp metal","Clamp metal","Clamp metal","Clamp metal","Clamp metal","Clamp metal"]
["","Insulation for fitting","","","Insulation for fitting","Insulation for fitting","Insulation for fitting","Insulation for fitting","Insulation for fitting","Insulation for fitting","Insulation for fitting","Insulation for fitting","Insulation for fitting"]
["","Sealing pads","","","Sealing pads","Sealing pads","Sealing pads","Sealing pads","Sealing pads","Sealing pads","Sealing pads","Sealing pads","Sealing pads"]
["","Clamps","","","Clamps","Clamps","Clamps","Clamps","Clamps","Clamps","Clamps","Clamps","Clamps"]
["","Screws","","","Screws","Screws","Screws","Screws","Screws","Screws","Screws","Screws","Screws"]
["","Washer","","","Washer","Washer","Washer","Washer","Washer","Washer","Washer","Washer","Washer"]
["Refrigerant","Type","","","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A"]
["Piping connections","Liquid","OD","mm","6.35","6.35","6.35","6.35","6.35","9.52","9.52","9.52","9.52"]
["","","Type","","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection"]
["","Gas","OD","mm","12.7","12.7","12.7","12.7","12.7","15.9","15.9","15.9","15.9"]
["","","Type","","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection"]
["","Drain","","","VP25 (I.D. 25/O.D. 32)","VP25 (I.D. 25/O.D. 32)","VP25 (I.D. 25/O.D. 32)","VP25 (I.D. 25/O.D. 32)","VP25 (I.D. 25/O.D. 32)","VP25 (I.D. 25/O.D. 32)","VP25 (I.D. 25/O.D. 32)","VP25 (I.D. 25/O.D. 32)","VP25 (I.D. 25/O.D. 32)"]
["Dimensions","Unit","Width","mm","550","550","550","700","700","1,000","1,400","1,400","1,400"]
["","","Depth","mm","800","800","800","800","800","800","800","800","800"]
["","","Height","mm","300","300","300","300","300","300","300","300","300"]
["Casing","Material","","","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate"]
["Weight","Unit","","kg","30","30","30","30","31","41","51","51","52"]
["Fan","External static pressure - 50Hz","High","Pa","88","88","64","88","88","88","113","107","78"]
["","","Low","Pa","20","20","15","20","29","20"]
["","External static pressure - 60Hz","High","Pa","73","73","86","88","88","122","147","136","78"]
["","","Low","Pa","10","10","10","10","10","10"]
["Decoration panel","Weight","","kg","3","3","3","3.5","3.5","4.5","6.5","6.5","6.5"]
["","Model","","","BYBS32DJW1","BYBS32DJW1","BYBS32DJW1","BYBS45DJW1","BYBS45DJW1","BYBS71DJW1","BYBS125DJW1","BYBS125DJW1","BYBS125DJW1"]
["","Dimensions","Height","mm","55","55","55","55","55","55","55","55","55"]
["","","Depth","mm","500","500","500","500","500","500","500","500","500"]
["","","Width","mm","650","650","650","800","800","1,100","1,500","1,500","1,500"]
["","Colour","","","White (10Y9/0.5)","White (10Y9/0.5)","White (10Y9/0.5)","White (10Y9/0.5)","White (10Y9/0.5)","White (10Y9/0.5)","White (10Y9/0.5)","White (10Y9/0.5)","White (10Y9/0.5)"]
["Current - 50Hz","Maximum fuse amps (MFA)","","A","15","15","15","15","15","15","15","15","15"]
["Power supply","Phase","","","1~","1~","1~","1~","1~","1~","1~","1~","1~"]
["","Name","","","VE","VE","VE","VE","VE","VE","VE","VE","VE"]
["","Frequency","","Hz","50/60","50/60","50/60","50/60","50/60","50/60","50/60","50/60","50/60"]
["","Voltage","","V","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220"]
["Notes","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)"]
["","","","","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)"]
["","","","","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat."]
["","","","","(4) - The external static pressure is changeable: change the connectors inside the electrical box, this pressure means: High static pressure - Standard - Low static pressure","(4) - The external static pressure is changeable: change the connectors inside the electrical box, this pressure means: High static pressure - Standard - Low static pressure","(4) - The external static pressure is changeable: change the connectors inside the electrical box, this pressure means: High static pressure - Standard - Low static pressure","(4) - The external static pressure is changeable: change the connectors inside the electrical box, this pressure means: High static pressure - Standard - Low static pressure","(4) - The external static pressure is changeable: change the connectors inside the electrical box, this pressure means: High static pressure - Standard - Low static pressure","(4) - The external static pressure is changeable: change the connectors inside the electrical box, this pressure means: High static pressure - Standard - Low static pressure","(4) - The external static pressure is changeable: change the connectors inside the electrical box, this pressure means: High static pressure - Standard - Low static pressure","(4) - The external static pressure is changeable: change the connectors inside the electrical box, this pressure means: High static pressure - Standard - Low static pressure","(4) - The external static pressure is changeable: change the connectors inside the electrical box, this pressure means: High static pressure - Standard - Low static pressure"]
["","","","","(5) - The external static pressure is changeable: change the connectors inside the electrical box, this pressure means: High static pressure - Standard","(5) - The external static pressure is changeable: change the connectors inside the electrical box, this pressure means: High static pressure - Standard","(5) - The external static pressure is changeable: change the connectors inside the electrical box, this pressure means: High static pressure - Standard","(5) - The external static pressure is changeable: change the connectors inside the electrical box, this pressure means: High static pressure - Standard","(5) - The external static pressure is changeable: change the connectors inside the electrical box, this pressure means: High static pressure - Standard","(5) - The external static pressure is changeable: change the connectors inside the electrical box, this pressure means: High static pressure - Standard","(5) - The external static pressure is changeable: change the connectors inside the electrical box, this pressure means: High static pressure - Standard","(5) - The external static pressure is changeable: change the connectors inside the electrical box, this pressure means: High static pressure - Standard","(5) - The external static pressure is changeable: change the connectors inside the electrical box, this pressure means: High static pressure - Standard"]
["","","","","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","(8) - MCA/MFA: MCA = 1.25 x FLA","(8) - MCA/MFA: MCA = 1.25 x FLA","(8) - MCA/MFA: MCA = 1.25 x FLA","(8) - MCA/MFA: MCA = 1.25 x FLA","(8) - MCA/MFA: MCA = 1.25 x FLA","(8) - MCA/MFA: MCA = 1.25 x FLA","(8) - MCA/MFA: MCA = 1.25 x FLA","(8) - MCA/MFA: MCA = 1.25 x FLA","(8) - MCA/MFA: MCA = 1.25 x FLA"]
["","","","","(9) - MFA ≤ 4 x FLA","(9) - MFA ≤ 4 x FLA","(9) - MFA ≤ 4 x FLA","(9) - MFA ≤ 4 x FLA","(9) - MFA ≤ 4 x FLA","(9) - MFA ≤ 4 x FLA","(9) - MFA ≤ 4 x FLA","(9) - MFA ≤ 4 x FLA","(9) - MFA ≤ 4 x FLA"]
["","","","","(10) - Next lower standard fuse rating minimum 15A","(10) - Next lower standard fuse rating minimum 15A","(10) - Next lower standard fuse rating minimum 15A","(10) - Next lower standard fuse rating minimum 15A","(10) - Next lower standard fuse rating minimum 15A","(10) - Next lower standard fuse rating minimum 15A","(10) - Next lower standard fuse rating minimum 15A","(10) - Next lower standard fuse rating minimum 15A","(10) - Next lower standard fuse rating minimum 15A"]
["","","","","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA"]
["","","","","(12) - Instead of a fuse, use a circuit breaker","(12) - Instead of a fuse, use a circuit breaker","(12) - Instead of a fuse, use a circuit breaker","(12) - Instead of a fuse, use a circuit breaker","(12) - Instead of a fuse, use a circuit breaker","(12) - Instead of a fuse, use a circuit breaker","(12) - Instead of a fuse, use a circuit breaker","(12) - Instead of a fuse, use a circuit breaker","(12) - Instead of a fuse, use a circuit breaker"]
["","","","","(13) - 220V","(13) - 220V","(13) - 220V","(13) - 220V","(13) - 220V","(13) - 220V","(13) - 220V","(13) - 220V","(13) - 220V"]
["","","","","(14) - 240V","(14) - 240V","(14) - 240V","(14) - 240V","(14) - 240V","(14) - 240V","(14) - 240V","(14) - 240V","(14) - 240V"]
["","","","","(15) - 220V, 50Hz","(15) - 220V, 50Hz","(15) - 220V, 50Hz","(15) - 220V, 50Hz","(15) - 220V, 50Hz","(15) - 220V, 50Hz","(15) - 220V, 50Hz","(15) - 220V, 50Hz","(15) - 220V, 50Hz"]
["","","","","(16) - 220V, 60Hz","(16) - 220V, 60Hz","(16) - 220V, 60Hz","(16) - 220V, 60Hz","(16) - 220V, 60Hz","(16) - 220V, 60Hz","(16) - 220V, 60Hz","(16) - 220V, 60Hz","(16) - 220V, 60Hz"]