{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":61,"n_cols":10,"rows_kept":61,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RZQG-L9V1"]
[]
[]
[]
[]
["","","","","","RZQG71L9V1B_AMB","RZQG71L9V1B","RZQG100L9V1B","RZQG125L9V1B","RZQG140L9V1B"]
["Sound pressure level","Heating","","High","dBA","12"]
["","","","Nom.","dBA","50","50","52","53","53"]
["","","","Low","dBA","12"]
["","Cooling","","Low","dBA","12"]
["","","","High","dBA","12"]
["","","","Nom.","dBA","48","48","50","51","52"]
["","Night quiet mode","","Level 1","dBA","43","43","45","45","45"]
["Refrigerant","Charge","","","TCO2Eq","6.1"]
["","GWP","","","","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5"]
["","Charge","","","kg","2.9","2.9","4.0","4.0","4.0"]
["","Type","","","","R-410A","R-410A","R-410A","R-410A","R-410A"]
["Fan motor","Output","","","W","94"]
["","Speed","Cooling","Super low","rpm","12"]
["","","Heating","Super low","rpm","12"]
["Operation range","Cooling","Ambient","Max.","°CDB","50","50.0","50.0","50.0","50.0"]
["","","","Min.","°CDB","-15","-15.0","-15.0","-15.0","-15.0"]
["","Heating","Ambient","Max.","°CWB","15.5","15.5","15.5","15.5","15.5"]
["","","","Min.","°CWB","-20","-20.0","-20.0","-20.0","-20.0"]
["Piping connections","Liquid","","OD","mm","","9.52","9.52","9.52","9.52"]
["","Level difference","IU - IU","Max.","m","0.5"]
["","","IU - OU","Max.","m","30.0"]
["","Additional refrigerant charge","","","kg/m","See installation manual"]
["","Total piping length","System","Actual","m","12"]
["Sound power level","Cooling","","","dBA","64","64.0","66.0","67.0","69.0"]
["","Heating","","","dBA","12","64.0","66.0","67.0","69.0"]
["Capacity control step","%","","","","100-0"]
["Dimensions","Unit","","Width","mm","940","940","940","940","940"]
["","","","Depth","mm","320","320","320","320","320"]
["","","","Height","mm","990","990","1,430","1,430","1,430"]
["Compressor","Type","","","","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing compressor"]
["Weight","Unit","","","kg","69"]
["Fan","Air flow rate","Heating","Super low","cfm","12.000"]
["","","","Super low","m³/min","12.000"]
["","","Cooling","Super low","m³/min","12.000"]
["","","","Super low","cfm","12.000"]
["Current - 50Hz","Maximum fuse amps (MFA)","","","A","","25","40","40","40"]
["Power supply","Phase","","","","1~","1~","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50","50","50"]
["","Voltage","","","V","220-240","220-240","220-240","220-240","220-240"]
["Notes","","","","","(1) - PED: assembly = category l : excluded from scope of PED due to article 1, item 3.6 of 97/23/EC","(1) - 3 with re-charging","(1) - 3 with re-charging","(1) - 3 with re-charging","(1) - 3 with re-charging"]
["","","","","","(2) - 3 with re-charging","(2) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current larger than 16A and ≤ 75A per phase.","(2) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current larger than 16A and ≤ 75A per phase.","(2) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current larger than 16A and ≤ 75A per phase.","(2) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current larger than 16A and ≤ 75A per phase."]
["","","","","","(3) - Minimum Ssc (=Short-circuit power) value: Equipment complying with EN/IEC 61000-3-12: European/International Technical Standard setting the limits for harmonic currents produced by equipment connected to public low-voltage systems with input current >16A and ≤ 75A per phase","(3) - Ssc: Short-circuit power","(3) - Ssc: Short-circuit power","(3) - Ssc: Short-circuit power","(3) - Ssc: Short-circuit power"]
["","","","","","(4) - See separate drawing for electrical data","(4) - PED: assembly = category l : excluded from scope of PED due to article 1, item 3.6 of 97/23/EC","(4) - PED: assembly = category l : excluded from scope of PED due to article 1, item 3.6 of 97/23/EC","(4) - PED: assembly = category l : excluded from scope of PED due to article 1, item 3.6 of 97/23/EC","(4) - PED: assembly = category l : excluded from scope of PED due to article 1, item 3.6 of 97/23/EC"]
["","","","","","(5) - Contains fluorinated greenhouse gases","(5) - See separate drawing for electrical data","(5) - See separate drawing for electrical data","(5) - See separate drawing for electrical data","(5) - See separate drawing for electrical data"]
["","","","","","(6) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker). For more detailed information on each combination, please refer to the electrical data drawing.","(6) - EN/IEC 61000-3-11: European/international technical standard setting the limits for voltage changes, voltage fluctuations and flicker in public low-voltage supply systems for equipment with rated ≤ 75A","(6) - EN/IEC 61000-3-11: European/international technical standard setting the limits for voltage changes, voltage fluctuations and flicker in public low-voltage supply systems for equipment with rated ≤ 75A","(6) - EN/IEC 61000-3-11: European/international technical standard setting the limits for voltage changes, voltage fluctuations and flicker in public low-voltage supply systems for equipment with rated ≤ 75A","(6) - EN/IEC 61000-3-11: European/international technical standard setting the limits for voltage changes, voltage fluctuations and flicker in public low-voltage supply systems for equipment with rated ≤ 75A"]
["Weight","Unit","","","kg","","69.0","95.0","95.0","95.0"]
["Piping connections","Gas","","OD","mm","","15.9","15.9","15.9","15.9"]
["","Piping length","OU - IU","Max.","m","","50","75","75","75"]
["","","System","Equivalent","m","","70","90","90","90"]
["","","","Chargeless","m","","30","30","30","30"]
["","Additional refrigerant charge","","","kg/m","","See installation manual","See installation manual","See installation manual","See installation manual"]
["","Level difference","IU - OU","Max.","m","","30.0","30.0","30.0","30.0"]
["","","IU - IU","Max.","m","","0.5","0.5","0.5","0.5"]
["Standard Accessories","Tie-wraps","","","","","2","2","2","2"]
["","Installation manual","","","","","1","1","1","1"]