{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":51,"n_cols":30,"rows_kept":51,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWFH-TZXSD"]
[]
[]
[]
[]
["","","","","","","EWFH220TZXSD1","EWFH230TZXSD1","EWFH275TZXSD1","EWFH300TZXSD1","EWFH350TZXSD1","EWFH400TZXSD1","EWFH465TZXSD2","EWFH470TZXSD1","EWFH515TZXSD1","EWFH540TZXSD1","EWFH545TZXSD2","EWFH600TZXSD2","EWFH620TZXSD1","EWFH645TZXSD2","EWFH700TZXSD2","EWFH750TZXSD2","EWFH790TZXSD2","EWFH840TZXSD2","EWFH900TZXSD2","EWFH975TZXSD2","EWFHH10TZXSD2","EWFHH11TZXSD2","EWFHH12TZXSD2","EWFHH13TZXSD2"]
["Puissance frigorifique","Nom.","","","","kW","294.3","316.33","373.77","409.14","472.71","537.62","639.32","627.11","680.63","712.06","745.73","817.28","819.29","876.96","941.65","1013.62","1071.7","1139.2","1210.17","1312.24","1468.78","1564.68","1682.27","1812.01"]
["Commande de puissance","Méthode","","","","","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance"]
["","Puissance minimale","","","","%","21.5","20","17.5","16","25","21.5","10","19","16.5","30","10","10","25","13.5","12.5","11.5","11.5","10.5","10","10","10","13.5","12.5","11.5"]
["Puissance absorbée","Rafraîchissement","","","Nom.","kW","82.95","94.88","98.33","116.83","118.56","150.72","157.39","172.19","195.92","182.44","183.18","220.47","241.68","230.72","256.58","267.38","271.32","303.46","341.95","375.79","416.08","422.09","463.18","521.59"]
["EER","","","","","","3.55","3.33","3.8","3.5","3.99","3.57","4.06","3.64","3.47","3.9","4.07","3.71","3.39","3.8","3.67","3.79","3.95","3.75","3.54","3.49","3.53","3.71","3.63","3.47"]
["IPLV (valeur intégrée sous charge partielle)","","","","","","6.046","6.019","6.119","6.101","6.701","6.28","6.277","6.571","6.45","6.125","6.389","6.3","5.832","6.479","6.362","6.639","6.69","6.489","6.472","6.443","6.436","6.376","6.481","6.426"]
["SEER","","","","","","5.493","5.444","5.544","5.609","6.003","5.967","5.8","6.11","5.704","5.444","5.912","5.831","5.379","5.957","5.918","6.147","6.205","6.127","6.008","6.025","5.997","5.645","5.693","5.758"]
["Dimensions","Unité","","","Profondeur","mm","2560","2560","3640","3640","4720","4720","6880","5800","5800","5800","6880","6880","5800","6880","6880","7960","9040","9040","9040","10120","11200","11200","12280","13360"]
["","","","","Hauteur","mm","2553","2553","2553","2553","2553","2553","2553","2553","2553","2553","2553","2553","2553","2553","2553","2553","2553","2553","2553","2553","2553","2553","2553","2553"]
["","","","","Largeur","mm","2238","2238","2238","2238","2238","2238","2238","2238","2238","2238","2238","2238","2238","2238","2238","2238","2238","2238","2238","2238","2238","2238","2238","2238"]
["Poids","Poids en fonctionnement","","","","kg","3054","3054","3679","3684","4552.7","4562.7","5841","5243.1","5248.1","6043.3","6230","6406","6053.3","6668","6673","7920","8500","8505","8785","9370","11223","11906","12491","13081"]
["","Unité","","","","kg","2797","2797","3337","3337","4146","4146","5065","4720","4720","5474","5284","5336","5474","5593","5593","6358","6868","6868","6957","7466","8383","9051","9561","10070"]
["Caisson","Couleur","","","","","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire"]
["Caisson","Matériau","","","","","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte"]
["Échangeur de chaleur-eau / évaporateur","Type","","","","","Échangeur à plaques","Échangeur à plaques","Échangeur à plaques","Échangeur à plaques","Échangeur à plaques","Échangeur à plaques","Multitubulaire","Échangeur à plaques","Échangeur à plaques","Échangeur à plaques","Multitubulaire","Multitubulaire","Échangeur à plaques","Multitubulaire","Multitubulaire","Multitubulaire","Multitubulaire","Multitubulaire","Multitubulaire","Multitubulaire","Multitubulaire","Multitubulaire","Multitubulaire","Multitubulaire"]
["","Échangeur de chaleur-eau / évaporateur-=-Volume d'eau-=-L","","","","L","40","40","48","48","42.7","42.7","152","58.1","58.1","76.3","232","289","76.3","289","289","492","492","492","583","583","1011","1011","1011","1011"]
["Échangeur de chaleur eau - évaporateur","Échangeur de chaleur eau - évaporateur-=-Chute de pression d'eau","","Échangeur de chaleur eau - évaporateur-=-Chute de pression d'eau-=-Rafraîchissement","Échangeur de chaleur eau - évaporateur-=-Chute de pression d'eau-=-Rafraîchissement-=-Nom.-=-kPa","kPa","10.07","11.38","12.82","14.98","32.32","41.04","38.4","30.52","35.79","23.43","35.27","31.07","30.05","34.82","39.11","46.95","51.05","56.41","51.29","58.44"]
["Échangeur de chaleur air","Type","","","","","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal"]
["Ventilateur","Quantité","","","","","4","4","6","6","8","8","12","10","10","10","12","12","10","12","12","14","16","16","16","18","20","20","22","24"]
["Ventilateur","Type","","","","","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct"]
["Ventil.","Débit d'air","","Rafraîchissement","Nom.","l/s","22510","22510","33765","33765","45020","45020","67530","56275","56275","56275","67530","67530","56275","67530","67530","78785","90040","90040","90040","101295","112550","112550","123805","135060"]
["Moteur de ventilateur","Entraînement","","","","","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai"]
["Compresseur","Compresseur-=-Quantité_","","","","","1","1","1","1","1","1","2","1","1","1","2","2","1","2","2","2","2","2","2","2","2","2","2","2"]
["Compresseur","Type","","","","","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis"]
["Plage de fonctionnement","Côté air","","Rafraîchissement","Min.","°CBS","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20"]
["","","","","Max.","°CBS","46","46","46","46","46","46","46","46","46","46","46","46","46","46","46","46","46","46","46","46","46","46","46","46"]
["","Côté eau","","Plage de fonctionnement-=-Côté eau-=-Rafraîchissement","Plage de fonctionnement-=-Côté eau-=-Rafraîchissement-=-Min.-=-°CBS","°CBS","4","4","4","4","4","4","4","4","4","4","4","4","4","4","4","4","4","4","4","4","4","4","4","4"]
["","","","","Plage de fonctionnement-=-Côté eau-=-Rafraîchissement-=-Max.-=-°CBS","°CBS","18","18","18","18","18","18","18","18","18","18","18","18","18","18","18","18","18","18","18","18","18","18","18","18"]
["Niveau de puissance sonore","Rafraîchissement","","","Nom.","dBA","97.3","97.5","100.2","100.9","97.3","99.8","100.6","104.5","101.7","98.8","100.9","105.5","100.6","98.1","100.1","100.9","101.5","102.8","105.1","106.9","104.7","102.7","103.6","104.5"]
["Niveau de pression sonore","Rafraîchissement","","","Nom.","dBA","78.1","78.4","80.4","81.1","77","79.6","79.4","83.8","81","78.1","79.8","84.3","79.8","76.9","78.9","79.3","79.6","80.9","83.2","84.6","82.2","80.1","80.8","81.4"]
["Réfrigérant","Type","","","","","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)"]
["Réfrigérant","PRP","","","","","7","7","7","7","7","7","7","7","7","7","7","7","7","7","7","7","7","7","7","7","7","7","7","7"]
["Réfrigérant","Charge","","","","kg","30","30","35","40","45","55","65","65","70","75","75","85","85","90","95","105","110","115","125","135","150","165","175","190"]
["","Circuits","","","Quantité","","1","1","1","1","1","1","2","1","1","1","2","2","1","2","2","2","2","2","2","2","2","2","2","2"]
["Raccords de tuyauterie","Entrée/Sortie d'eau de l'évaporateur (DE)","","","","","88.9","88.9","88.9","88.9","139.7","139.7","139.7","139.7","139.7","139.7","168.3","168.3","139.7","168.3","168.3","219.1","219.1","219.1","219.1","219.1","273","273","273","273"]
["Alimentation électrique","Phase","","","","","3","3","3","3","3","3","3","3","3","3","3","3","3","3","3","3","3","3","3","3","3","3","3","3"]
["","Alimentation électrique-=-Fréquence","","","Fréquence","","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50"]
["","Alimentation électrique-=-Tension","","","Alimentation électrique-=-Tension-=-V","","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400"]
["","Plage de tension","","Min.","Min.","","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10"]
["","","","Max.","Max.","","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10"]
["Unité","Courant de démarrage","","Unité-=-Courant de démarrage-=-Max.","Max.","","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["","Courant de service","Rafraîch.","Unité-=-Courant de service-=-Rafraîch.-=-Nom.","Nom.","","135","153","161","188","197","245","257","277","312","296","295","357","385","384","423","439","445","493","550","601","661","678","739","826"]
["","","","Unité-=-Courant de service-=-Max.","Max.","","172","183","214","236","269","310","364","357","394","414","406","448","491","472","517","527","579","618","655","702","787","902","992","1090"]
["Unité","Unit-=-Max unit current for wires sizing","","","Courant max. d’unité pour déterminer la taille des fils","","190","201","235","259","296","340","401","393","434","456","442","492","541","520","569","580","637","680","721","772","866","992","1091","1198"]
["Échangeur de chaleur eau&nbsp;- évaporateur","Échangeur de chaleur eau&nbsp;- évaporateur-=-Chute de pression d'eau","","Échangeur de chaleur eau&nbsp;- évaporateur-=-Chute de pression d'eau-=-Rafraîchissement","Échangeur de chaleur eau&nbsp;- évaporateur-=-Chute de pression d'eau-=-Rafraîchissement-=-Nom.-=-kPa","kPa","","","","","","","","","","","","","","","","","","","","","30.4","48.85","54.18","41.49"]