{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":48,"n_cols":9,"rows_kept":48,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWC-BF"]
[]
[]
[]
[]
["","","","","","FWC06B5FV1B","FWC07B5FV1B","FWC08B5FV1B","FWC09B5FV1B"]
["Niveau de pression sonore","Bas","","","dBA","21.0","22.0","24.0","28.0"]
["","Haut","","","dBA","29.0","33.0","39.0","43.0"]
["Accessoires standard","Manuel d'installation et d'exploitation","","","","1","1","1","1"]
["","Guide d'installation","","","","1","1","1","1"]
["","Flexible d'évacuation","","","","1","1","1","1"]
["","Bride métallique pour flexible d'évacuation","","","","1","1","1","1"]
["","Rondelle pour attache de suspension","","","","8","8","8","8"]
["","Vis","","","","4","4","4","4"]
["","Joint torique","","","","4","4","4","4"]
["","Isolation","","","","6","6","6","6"]
["Niveau de puissance sonore totale","Bas","","","dBA","33.0","36.0","36.0","40.0"]
["","Haut","","","dBA","43.0","47.0","53.0","57.0"]
["Débit d'eau","Chute de pression d'eau","Chauffage","Haut","kPa","18","22","30","38"]
["","","Rafraîchissement","Haut","kPa","15","18","23","30"]
["Raccords de tuyauterie","Évacuation","","DE","mm","VP25 (diamètre ext. : 32 / diamètre int. : 25)","VP25 (diamètre ext. : 32 / diamètre int. : 25)","VP25 (diamètre ext. : 32 / diamètre int. : 25)","VP25 (diamètre ext. : 32 / diamètre int. : 25)"]
["","Eau","","Entrée","","3/4\" BSP (filetage femelle)","3/4\" BSP (filetage femelle)","3/4\" BSP (filetage femelle)","3/4\" BSP (filetage femelle)"]
["","","","Sortie","","3/4\" BSP (filetage femelle)","3/4\" BSP (filetage femelle)","3/4\" BSP (filetage femelle)","3/4\" BSP (filetage femelle)"]
["Puissance absorbée","Haut","","","kW","0.046","0.055","0.077","0.107"]
["","Bas","","","kW","0.035","0.038","0.040","0.046"]
["Température d'eau autorisée","Chauffage","","Max.","°C","70 (4)","70 (4)","70 (4)","70 (4)"]
["","","","Min.","°C","5 (4)","5 (4)","5 (4)","5 (4)"]
["","Rafraîchissement","","Min.","°C","5 (4)","5 (4)","5 (4)","5 (4)"]
["","","","Max.","°C","70 (4)","70 (4)","70 (4)","70 (4)"]
["Dimensions","Unité","","Largeur","mm","840","840","840","840"]
["","","","Profondeur","mm","840","840","840","840"]
["","","","Hauteur","mm","288","288","288","288"]
["Poids","Unité","","","kg","29","29","29","29"]
["Ventilateur","Débit d’air","","Bas","m³/h","708","804","852","1,014"]
["","","","Haut","m³/h","1,032","1,200","1,476","1,746"]
["Puissance frigorifique (conditions standards)","Puissance totale (4 tuyaux)","","Bas","kW","4.3 (1)","4.6 (1)","4.8 (1)","5.7 (1)"]
["","","","Haut","kW","5.9 (1)","6.3 (1)","7.2 (1)","8.3 (1)"]
["","Puissance sensible (4 tuyaux)","","Bas","kW","3.1 (1)","3.3 (1)","3.5 (1)","4.0 (1)"]
["","","","Haut","kW","4.2 (1)","4.6 (1)","5.4 (1)","6.4 (1)"]
["Puissance calorifique (conditions standards)","Puissance (4 tuyaux)","","Bas","kW","5.2 (3)","5.5 (3)","5.8 (3)","6.8 (3)"]
["","","","Haut","kW","6.9 (3)","7.8 (3)","9.2 (3)","10.4 (3)"]
["Power supply","Phase","","","","1~","1~","1~","1~"]
["","Fréquence","","","Hz","50","50","50","50"]
["","Tension","","","V","220-240","220-240","220-240","220-240"]
["Remarques","","","","","(1) - Rafraîchissement: air 27 °CBS, 19 °CBH ; eau à l'entrée 7 °C ; eau en sortie 12 °C","(1) - Rafraîchissement: air 27 °CBS, 19 °CBH ; eau à l'entrée 7 °C ; eau en sortie 12 °C","(1) - Rafraîchissement: air 27 °CBS, 19 °CBH ; eau à l'entrée 7 °C ; eau en sortie 12 °C","(1) - Rafraîchissement: air 27 °CBS, 19 °CBH ; eau à l'entrée 7 °C ; eau en sortie 12 °C"]
["","","","","","(2) - Chauffage : 2 tuyaux : air 20°C BS, 15°C BH ; entrée d'eau 45°C ; sortie d’eau 40°C","(2) - Chauffage : 2 tuyaux : air 20°C BS, 15°C BH ; entrée d'eau 45°C ; sortie d’eau 40°C","(2) - Chauffage : 2 tuyaux : air 20°C BS, 15°C BH ; entrée d'eau 45°C ; sortie d’eau 40°C","(2) - Chauffage : 2 tuyaux : air 20°C BS, 15°C BH ; entrée d'eau 45°C ; sortie d’eau 40°C"]
["","","","","","(3) - Chauffage : 4 tuyaux : air 20°C BS, 15°C BH ; entrée d'eau 65°C ; sortie d’eau 55°C","(3) - Chauffage : 4 tuyaux : air 20°C BS, 15°C BH ; entrée d'eau 65°C ; sortie d’eau 55°C","(3) - Chauffage : 4 tuyaux : air 20°C BS, 15°C BH ; entrée d'eau 65°C ; sortie d’eau 55°C","(3) - Chauffage : 4 tuyaux : air 20°C BS, 15°C BH ; entrée d'eau 65°C ; sortie d’eau 55°C"]
["","","","","","(4) - Ne pas laisser d'eau à température inférieure à 5 °C ou supérieure à 50/70 °C pénétrer dans l'unité, au risque d'endommager cette dernière.","(4) - Ne pas laisser d'eau à température inférieure à 5 °C ou supérieure à 50/70 °C pénétrer dans l'unité, au risque d'endommager cette dernière.","(4) - Ne pas laisser d'eau à température inférieure à 5 °C ou supérieure à 50/70 °C pénétrer dans l'unité, au risque d'endommager cette dernière.","(4) - Ne pas laisser d'eau à température inférieure à 5 °C ou supérieure à 50/70 °C pénétrer dans l'unité, au risque d'endommager cette dernière."]