{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":42,"n_cols":9,"rows_kept":42,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWC-BT"]
[]
[]
[]
[]
["","","","","","FWC06B5TV1B","FWC07B5TV1B","FWC08B5TV1B","FWC09B5TV1B"]
["Niveau de pression sonore","Bas","","","dBA","21.0","22.0","24.0","28.0"]
["","Haut","","","dBA","29.0","33.0","39.0","43.0"]
["Accessoires standard","Manuel d'installation et d'exploitation","","","","1","1","1","1"]
["","Guide d'installation","","","","1","1","1","1"]
["","Flexible d'évacuation","","","","1","1","1","1"]
["","Bride métallique pour flexible d'évacuation","","","","1","1","1","1"]
["","Rondelle pour attache de suspension","","","","8","8","8","8"]
["","Vis","","","","4","4","4","4"]
["","Joint torique","","","","2","2","2","2"]
["","Isolation","","","","4","4","4","4"]
["Niveau de puissance sonore totale","Bas","","","dBA","31.0","33.0","36.0","40.0"]
["","Haut","","","dBA","43.0","47.0","53.0","57.0"]
["Débit d'eau","Chute de pression d'eau","Chauffage","Haut","kPa","17","22","29","37"]
["","","Rafraîchissement","Haut","kPa","15","18","24","30"]
["Raccords de tuyauterie","Évacuation","","OD","mm","VP25 (diamètre ext. : 32 / diamètre int. : 25)","VP25 (diamètre ext. : 32 / diamètre int. : 25)","VP25 (diamètre ext. : 32 / diamètre int. : 25)","VP25 (diamètre ext. : 32 / diamètre int. : 25)"]
["","Eau","","Entrée","","3/4\" BSP (filetage femelle)","3/4\" BSP (filetage femelle)","3/4\" BSP (filetage femelle)","3/4\" BSP (filetage femelle)"]
["","","","Sortie","","3/4\" BSP (filetage femelle)","3/4\" BSP (filetage femelle)","3/4\" BSP (filetage femelle)","3/4\" BSP (filetage femelle)"]
["Puissance absorbée","Haut","","","kW","0.045","0.054","0.077","0.107"]
["","Bas","","","kW","0.034","0.037","0.039","0.045"]
["Température d'eau autorisée","Chauffage","","Max.","°C","50 (4)","50 (4)","50 (4)","50 (4)"]
["","","","Min.","°C","5 (4)","5 (4)","5 (4)","5 (4)"]
["","Rafraîchissement","","Min.","°C","5 (4)","5 (4)","5 (4)","5 (4)"]
["","","","Max.","°C","50 (4)","50 (4)","50 (4)","50 (4)"]
["Dimensions","Unité","","Largeur","mm","840","840","840","840"]
["","","","Profondeur","mm","840","840","840","840"]
["","","","Hauteur","mm","288","288","288","288"]
["Poids","Unité","","","kg","26","26","26","26"]
["Ventilateur","Débit d'air","","Bas","m³/h","720","834","888","1,044"]
["","","","Haut","m³/h","1,068","1,236","1,518","1,776"]
["Power supply","Phase","","","","1~","1~","1~","1~"]
["","Fréquence","","","Hz","50","50","50","50"]
["","Tension","","","V","220-240","220-240","220-240","220-240"]
["Remarques","","","","","(1) - Rafraîchissement: air 27 °CBS, 19 °CBH ; eau à l'entrée 7 °C ; eau en sortie 12 °C","(1) - Rafraîchissement: air 27 °CBS, 19 °CBH ; eau à l'entrée 7 °C ; eau en sortie 12 °C","(1) - Rafraîchissement: air 27 °CBS, 19 °CBH ; eau à l'entrée 7 °C ; eau en sortie 12 °C","(1) - Rafraîchissement: air 27 °CBS, 19 °CBH ; eau à l'entrée 7 °C ; eau en sortie 12 °C"]
["","","","","","(2) - Chauffage : 2 tuyaux : air 20°C BS, 15°C BH ; entrée d'eau 45°C ; sortie d’eau 40°C","(2) - Chauffage : 2 tuyaux : air 20°C BS, 15°C BH ; entrée d'eau 45°C ; sortie d’eau 40°C","(2) - Chauffage : 2 tuyaux : air 20°C BS, 15°C BH ; entrée d'eau 45°C ; sortie d’eau 40°C","(2) - Chauffage : 2 tuyaux : air 20°C BS, 15°C BH ; entrée d'eau 45°C ; sortie d’eau 40°C"]
["","","","","","(3) - Chauffage : 4 tuyaux : air 20°C BS, 15°C BH ; entrée d'eau 65°C ; sortie d’eau 55°C","(3) - Chauffage : 4 tuyaux : air 20°C BS, 15°C BH ; entrée d'eau 65°C ; sortie d’eau 55°C","(3) - Chauffage : 4 tuyaux : air 20°C BS, 15°C BH ; entrée d'eau 65°C ; sortie d’eau 55°C","(3) - Chauffage : 4 tuyaux : air 20°C BS, 15°C BH ; entrée d'eau 65°C ; sortie d’eau 55°C"]
["","","","","","(4) - Ne pas laisser d'eau à température inférieure à 5 °C ou supérieure à 50/70 °C pénétrer dans l'unité, au risque d'endommager cette dernière.","(4) - Ne pas laisser d'eau à température inférieure à 5 °C ou supérieure à 50/70 °C pénétrer dans l'unité, au risque d'endommager cette dernière.","(4) - Ne pas laisser d'eau à température inférieure à 5 °C ou supérieure à 50/70 °C pénétrer dans l'unité, au risque d'endommager cette dernière.","(4) - Ne pas laisser d'eau à température inférieure à 5 °C ou supérieure à 50/70 °C pénétrer dans l'unité, au risque d'endommager cette dernière."]