{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":74,"n_cols":9,"rows_kept":74,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RZAG-MV1"]
[]
[]
[]
[]
["","","","","","RZAG71M7V1B","RZAG100M7V1B","RZAG125M7V1B","RZAG140M7V1B"]
["Niveau de pression sonore","Chauffage","","Nom.","dBA","","","","52"]
["","Rafraîchissement","","Nom.","dBA","","","","51"]
["Accessoires standard","Attaches","","","","","","","2"]
["","Manuel d'installation","","","","","","","1"]
["","Étiquette de réfrigérant pour réglementation F-gas","","","","","","","1"]
["","Précautions générales de sécurité","","","","","","","1"]
["","Étiquette énergétique LOT10","","","","","","","1"]
["Réfrigérant","Charge","","","TCO2Eq","","","","2.53"]
["","PRP","","","","","","","675"]
["","Charge","","","kg","","","","3.75"]
["","Type","","","","","","","R-32"]
["Raccordements de tuyauterie","Liquide","","DE","mm","","","","9.52"]
["","Longueur de tuyauterie","Max.","UE - UI","m","","","","85"]
["","","Système","Préchargé d'usine jusqu'à","m","","","","40"]
["","","","Équivalente","m","","","","100"]
["","Gaz","","DE","mm","","","","15.9"]
["","Dénivelé","UI - UI","Max.","m","","","","0.5"]
["","","UI - UE","Max.","m","","","","30.0"]
["","Charge de réfrigérant supplémentaire","","","kg/m","","","","Voir le manuel d'installation"]
["Sound power level","Rafraîchissement","","","dBA","","","","70"]
["","Chauffage","","","dBA","","","","70 (1)"]
["Compresseur","Type","","","","","","","Compresseur swing hermétique"]
["Dimensions","Unité","","Largeur","mm","","","","940"]
["","","","Profondeur","mm","","","","320"]
["","","","Hauteur","mm","","","","1,430"]
["Poids","Unité","","","kg","","","","92"]
["Power supply","Phase","","","","","","","1~"]
["","Fréquence","","","Hz","","","","50"]
["","Tension","","","V","","","","220-240"]
["Remarques","","","","","","","","(1) - Conforme à la norme ENER Lot 21"]
["","","","","","","","","(2) - Norme technique internationale/européenne définissant les limites de courants harmoniques générés par les équipements connectés au système basse tension public avec un courant d'entrée supérieur à 16 A et ≤ 75 A par phase."]
["","","","","","","","","(3) - Ssc : puissance de court-circuit"]
["","","","","","","","","(4) - Norme technique internationale/européenne définissant les limites de courants harmoniques générés par les équipements connectés au système basse tension public avec un courant d'entrée ≤ 16 A par phase."]
["Dimensions","Unité","","Hauteur","mm","990","1430","1430"]
["","","","Largeur","mm","940","940","940"]
["","","","Profondeur","mm","320","320","320"]
["Poids","Unité","","","kg","70","92","92"]
["Compresseur","Type","","","","Compresseur swing hermétique","Compresseur swing hermétique","Compresseur swing hermétique"]
["Plage de fonctionnement","Rafraîchissement","Temp. ext.","Min.","°CBS","-20","-20","-20"]
["","","","Max.","°CBS","52","52","52"]
["","Chauffage","Temp. ext.","Min.","°CBH","-20","-20","-20"]
["","","","Max.","°CBH","18.0","18.0","18.0"]
["Niveau de puissance sonore","Rafraîchissement","","","dBA","64","66","69"]
["Niveau de pression sonore","Rafraîchissement","","Nom.","dBA","46","47","50"]
["","Chauffage","","Nom.","dBA","49","51","52"]
["Réfrigérant","","","","","R-32","R-32","R-32"]
["","Charge","","","kg","2.95","3.75","3.75"]
["","Réfrigérant-=-PRP","","","","675","675","675"]
["","Charge","","","tCO2Eq","1.99","2.53","2.53"]
["Raccords de tuyauterie","Liquide","","DE","mm","9.52","9.52","9.52"]
["","Gaz","","DE","mm","15.9","15.9","15.9"]
["","Longueur de tuyauterie","Max.","UE - UI","m","55","85","85"]
["","","Système","Équivalente","m","75","100","100"]
["","","","Préchargé d'usine jusqu'à","m","40","40","40"]
["","Charge de réfrigérant supplémentaire","","","kg/m","Voir le manuel d'installation","Voir le manuel d'installation","Voir le manuel d'installation"]
["","Dénivelé","UI - UE","Max.","m","30.0","30.0","30.0"]
["","","UI - UI","Max.","m","0.5","0.5","0.5"]
["Accessoires standard","Installation manual","","","","1","1","1"]
["","Refrigerant label for F-gas regulation","","","","1","1","1"]
["","General safety precautions","","","","1","1","1"]
["","LOT10 Energy Label","","","","1","1","1"]
["","Tie-wraps","","","","2","2","2"]
["Alimentation électrique","Phase","","","","1~","1~","1~"]
["","Fréquence","","","Hz","50","50","50"]
["","Alimentation électrique-=-Tension-=-V","","","V","220-240","220-240","220-240"]
["Courant&nbsp;- 50&nbsp;Hz","Courant&nbsp;- 50&nbsp;Hz-=-Intensité maximale de fusible (MFA)-=-A","","","A","20","32","32"]
["Niveau de puissance sonore","Chauffage","","","dBA","","","69 (1)"]
["Remarques","","","","","","","(1) - Conforme à la norme ENER Lot 21"]